ECE 472

POWER SYSTEMS II

EXPERIMENT 4 – WEEK 5

OVERCURRENT RELAYS

Objective

The objectives of this laboratory experiment are summarized below:

1. To become familiar with Schweitzer 151 relay.

2. To become familiar with connection of Schweitzer 151 relay to

a model power system.

3. Learn to perform measurements with Schweitzer 151 relay.

4. Learn to set Schweitzer 151 relay for line protection.

Pre - Lab

Familiarize yourself with the Schweitzer 151 relay instruction manual.

Figure 1 shows a one-line diagram of the three-phase model power system which consists of:

- Source

- Transformer

- 300 mile/320 kV radial line

- Resistor Bank

G

LOAD

R

Figure 1. Model Power System

The following are the data for this model power system:

VSource = 120 V (line-to-line)

Transformer Turns Ratio = 1

ZTransformer = 6.8 + j 1.17 Ω

ZLine = 6.9 + j 53.16 Ω

CLine = 0.94 μF

Perform calculation of the source current, line current, sending-end bus voltage, and receiving-end bus voltage of Figure 1 for the following cases:

Case 1: A resistive load of 150 Ω is connected to the receiving-end of transmission line

Case 2: A short circuit is placed across the load.

Document the magnitude and phase angle of the source current and the sending-end bus voltage for cases 1 and 2. Calculation of Case 2 provides the three-phase fault current at the end of the line. From the magnitude of the three-phase fault current, obtain the magnitude of the phase-to-phase fault current at the end of the line.

Procedure

A Schweitzer 151 overcurrent relay is connected to the sending-end of transmission line to protect the transmission line against short circuits. To test the proper operation of relay, turn on the source voltage and the load. Gradually increase the source voltage until you reach 120 V. Note that the line-to-line voltage is 120 volts. Therefore, the line-to-neutral voltage will be 69.28 V.  Also, turn on the three-phase 150 Ω resistors.

To connect the Schweitzer 151 relay to the lab PC, turn the relay on (you should hear relay clicking) and double-click on the SEL icon. Then perform the following:

- Type ACCESS

- Type OTTER which is your Level 1 password

- Type METER and observe the three-phase voltages and currents

- Type SHOWSET1 and observe the relevant settings of SEL 151V relay

- Type SET 1 to change settings of the relay, and document the relay message

- Type 2ACCESS

- Type TAIL which is your Level 2 password

- Type DATE mm/dd/yy

- Type TIME hh:mm:ss

- Type METER and document three-phase voltages, three-phase currents, and total three-phase real and reactive power. Confirm these values based on the current CTR and PTR settings, if possible

- Type SET 1 and perform the following:

  - Change the ID to ECE 472 and your names

  - Set the CTR to 1.

  - Set the PTR to 1

  - Set R1 to 6.9 ohms

  - Set X1 to 53.16 ohms

  - Set Line Length (LL) to 300 miles

  - Set the overcurrent phase relat setting (51P) for the phase-to-phase fault current at the end of the line

  - Type END

  - Type Y and you should hear relay clicking

- Short phases A and B by pushing the normally open switch down momentarily

(Read the ammeter current value while you are shorting the two phases)

- Document the relay message and confirm that the value of fault current is OK, if possible

- Type HIST

- Short phases B and C by rewiring the normally open switch and pushing it down    momentarily

- Document the relay message

- Type HIST

- Short phases C and A by rewiring the normally open switch and pushing it down    momentarily

- Document the relay message and confirm that the value of fault current is OK

- Type HIST

- Short phase A to Neutral by rewiring the normally open switch and pushing it down momentarily

- Document the relay message and confirm that the value of fault current is OK

- Type HIST

- Type QUIT and close the relay window

Turn the power supply voltage back to zero and shut the power off. Also, turn off the relay.

Documentation

Turn in a brief Memo about this experiment in a week from the experiment date. Attach all of the pre-lab calculations and computer printouts to your Memo.